SECTION 23 34 33

AIR CURTAINS

This specification includes Mars Air Systems Phantom 10 Series air curtains for environmental control, flying insect control, and temperature control. Heating options are available for electric, hot water, and steam.

Phantom 10 Series air curtains are available for openings 36 inches to 144 inches wide. Recommended installation heights are up to 12 feet for environmental separation and temperature control applications and up to 10 feet for flying insect control applications. Phantom Series air curtains are typically effective to resist wind loads up to 12 mph for temperature control applications. Note that velocities specified for each unit are based on a 60 Hz power source

Typical installations include commercial, office, and retail entrances. Air curtains help reduce heating and cooling costs while expediting the flow of traffic from one work area to another or in and out of a building. At the same time, air curtains can repel mild breeze and minimize the entrance of windborne dust, fumes, pollutants, and flying insects.

Mars Air Curtain products meet the requirements of all North American and European Union Codes and Standards. For a complete selection guide and assistance with your air curtain configuration, please visit www.marsair.com.

Important Note: This specification contains hidden text appearing in red. To show or remove hidden text in MSWord, click the “File” tab or “Office” icon on the top-left corner, select “Options,” select “Display,” and check or uncheck the box marked “Hidden Text.”

- GENERAL

  - SECTION INCLUDES

SPECIFIER NOTE – Delete items below not required for project.

    - Air curtains for pedestrian entrances.

    - Air curtains for vehicular entrances.

  - RELATED SECTIONS

SPECIFIER NOTE – Delete any sections below not relevant to this project; add others as required.

    - Section 05 50 00 – Metal Fabrications: Concealed steel support members.

    - Section 06 10 00 – Rough Carpentry.

    - Section 05 41 00 – Structural Metal Studs.

    - Section 07 62 00 – Sheet metal flashing.

    - Section 07 92 00 – Joint Sealants.

    - Section 08 10 00 – Metal Doors and Frames.

    - Section 08 33 00 – Overhead Coiling Doors.

    - Section 08 42 00 – Entrance Doors.

    - Section 22 10 00 – Plumbing Piping:

    - Section 23 21 00 – Hydronic Piping: Hot water heating piping to units.

    - Section 23 22 13- Steam and Condensate Piping: Steam heating piping to units.

    - Section 26 05 00 – Equipment Wiring: Connections to building power distribution.

  - REFERENCES

SPECIFIER NOTE – Delete items below not required for project.

    - ASTM A240 / A240M -10 – Standard Specification for Chromium and Chromium.

    - ASTM A591/A591M Standard Specification for Steel Sheet, Electrolytic Zinc-Coated, for Light Coating Weight Applications

    - ASTM B209 – Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

    - ASTM A879 / A879M -06 – Standard Specification for Steel Sheet, Zinc Coated by the Electrolytic Process for Application Requiring Designation of the Coating Mass on Each Surface.

    - UL 507 – UL Standard for Safety Electric Fans – Intertek Testing Services Listed for US and Canada.

    - AHRI 410-2001 – Standard for Forced-Circulation Air-cooling and Air-Heating Coils.

    - Electrical components UL/CUL listed.

    - AMCA 211 Certified

    - ELT

    - NEC – National Electric Code.

    - Meets NEC and CEC tested by ETL Certified to conform to UL2021(US) and CSA22.2 (Canada) Standards

    - UL/CUL listed

    - U.S. Green Building Council, LEED Building Design and Construction (BD+C) Version 4.0 Rating System. (LEED v4.0).

  - SUBMITTALS

    - Submit under provisions of Section 01 33 00.

    - Product Data: Manufacturer's data sheets on each product to be used, including:

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Installation methods.

    - Shop Drawings: Include plans, elevations, sections, and details, indicating dimensions, tolerances, materials, fasteners, hardware, finish, piping, electrical wiring diagrams, options, and accessories.

SPECIFIER NOTE – Delete the following paragraphs if LEED is not applicable. Review design-phase credits available related to tubular unit skylights, including contribution to IEQ Cr 6.1 Controllability of Systems, IEQ Cr 8.1. Daylighting, EA Cr 1 Energy Optimization, and ID Cr 1 Innovation in Design credits. Consult VELUX representative for detailed support data.

    - LEED Submittals: Provide documentation of how the requirements of Credit will be met:

      - List of proposed materials with recycled content. Indicate post-consumer recycled content and pre-consumer recycled content for each product having recycled content.

      - Product data and certification letter indicating percentages by weight of post-consumer and pre-consumer recycled content for products having recycled content.

SPECIFIER NOTE – Delete selection samples if colors have already been selected.

    - Selection Samples: For each finish product specified, two complete sets of color chips representing manufacturer's full range of available colors and patterns.

    - Verification Samples: For each finish product specified, two samples, minimum size 6.25 inches (160 mm) square, representing actual product, color, and patterns.

    - Manufacturer's Certificates: Certify products meet or exceed specified requirements.

    - Operation and Maintenance Manual: Submit manufacturer's operation and maintenance manual, including operation, maintenance, adjustment, and cleaning instructions, troubleshooting guide, parts list, and electrical wiring diagrams.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Minimum ten years documented experience producing the products specified in this Section

    - Installer Qualifications: Minimum five years documented experience installing products specified in this Section

  - DELIVERY, STORAGE, AND HANDLING

SPECIFIER NOTE – Delete items below not required for project.

    - Store products in manufacturer's unopened packaging until ready for installation.

    - Store in a dry, heated storage area until installation of products.

    - Protect materials and finish from damage during handling and installation.

  - SEQUENCING

SPECIFIER NOTE – Delete items below not required for project.

    - Ensure that locating templates and other information required for installation of products of this section are furnished to affected trades in time to prevent interruption of construction progress.

    - Coordinate the installation of wiring and control switches for air curtains with the openings and the hardware provided for such openings.

    - Install after doors, walls, ceilings, and other adjacent surfaces are finished and painted.

  - WARRANTY

SPECIFIER NOTE – Select the applicable warranty from the following paragraphs as required for the unit(s) specified and delete the one not required.

    - Standard five-year limited parts warranty for unheated units against defects in workmanship and material.

    - Standard 18-month limited parts warranty for heated units against defects in workmanship and materials.

- PRODUCTS

  - MANUFACTURER

    - Acceptable Manufacturer: Mars Air Systems, LLC; 14716 South Broadway St., Gardena, CA 90248. Tel: (310) 532-1555 or (800) 421-1266. Fax: (310) 324-3030. Email: info@marsair.com. Web: www.marsair.com.

    - Delete one of the following two paragraphs: coordinate with requirements of Division 1 section on product options and substitutions.

    - Requests for substitutions will be considered in accordance with provisions of Section 01 33 00.

SPECIFIER NOTE -Select the type and sizes required and delete those not required. Indicate the door/opening height for each air curtain on the Drawings or on the Schedule at the end of this Section. If more than one type and/or size is required, indicate the location of each on the Drawings or on the Schedule at the end of this Section.

  - AIR CURTAIN ASSEMBLIES

    - Motor Fan Assembly: Design for easy removal, assembly, repair, and maintenance.

      - Motor: Totally enclosed air over (TEAO) cooled motor with sealed lifetime pre-lubricated ball bearings, motor starter and thermal overload protection.

SPECIFIER NOTE – Select one of the following paragraphs and delete the ones not required. Single speed is standard.

        - Wired for single speed operation.

        - Wired for two speed operation.

        - Wired for three speed operation.

SPECIFIER NOTE – Select one of the following paragraphs as required for specialty motors and delete the one not required. Indicate the location of special use motors on the Drawings or on the Schedule at the end of this Section.

        - Provide wash down type motors, NEC IP-54 for the locations indicated.

        - Provide explosion proof type motors, NEC Class 1, Division 1, Group D for the locations indicated.

        - Meets NEC. ETL Listed to conform to UL 507 (US) and CSA22.2 (Canada) Standards. AMCA 211 Certified.

SPECIFIER NOTE – Select one of the following paragraphs and delete the ones not required. Note that Electrical Characteristics below do not include electric heater requirements. Note that all motors listed are based on 60 Hz service. For other voltages contact manufacturer.

        - Electrical Characteristics: 115V AC, single phase; 5.1 Amp full load per motor/fan.

        - Electrical Characteristics: 208/230V AC, single phase; 2.5 Amp full load per motor/fan.

        - Electrical Characteristics: 208/230V AC, three-phase; 1.8/1.6 Amp full load per motor/fan.

        - Electrical Characteristics: 460V AC, three-phase; 0.8 Amp full load per motor/fan.

        - Electrical Characteristics: 575V AC, three-phase; 0.65 Amp full load per motor/fan.

      - Fans: Forward curved centrifugal type, double width, and double inlet design, directly driven to an electric motor.

        - Provide resilient isolation dampening mountings between motor frame and motor mounting pan.

        - Factory balanced blower wheel assembly statically and dynamically.

    - Housing: Self-contained one-piece type for units up to 72 inches in length with sufficient strength for mounting from pre-punched mounting holes at both ends to ceiling without intermediate support. Units longer than 72” are two units tandem mounted next to each other

      - Size:

SPECIFIER NOTE – Select one of the following paragraphs and delete the ones not required. Heated units are mounted inside only; coordinate with heating paragraphs if required.

        - Unheated: 26 inches deep by 15-1/2 inches high by width of unit.

        - Electric Heated: 26 inches deep by 15-1/2 inches high by width of unit.

        - Hot Water/Steam Heated: 26 inches deep by 15-1/2 inches high by width of unit plus 10 inches for manifolds.

      - Mounting:

SPECIFIER NOTE – Select one of the following paragraphs and delete the ones not required. Heated units are mounted inside only; coordinate with heating paragraphs if required.

        - Unheated Inside Mount.

        - Heated Inside Mount.

        - Unheated Outside Mount.

        - Mount Location Indicated.

      - Material:

SPECIFIER NOTE – Select one of the following paragraphs and delete the one not required.

        - Provide T5052 20 gage aluminum conforming to ASTM B 209 and 20-gauge electro or hot dipped galvanized steel sheet housing conforming to ASTM A 591 and/or ASTM A 653.

        - Provide type 304 stainless steel housing with brushed finish. ASTM A 240/A 240M.

      - Air Inlet Grille and/or Filters: Provide air inlet grille and/or filters specified.

      - Discharge: Provide integral discharge nozzle specified.

SPECIFIER NOTE – Select following paragraph for sheet steel housings only. Delete entirely for stainless steel housing. Select color required for steel housing and delete the ones not required. Pearl White is standard.

      - Finish and Color: Provide with, no VOC, corrosion resistant polyurethane powder coated finish for sheet metal housings.

        - Pearl White.

        - Obsidian Black.

        - Titanium Silver.

        - Stainless Steel.

    - Environmental Air Curtains: Internal mounted models for heights up to 12 feet (3658 mm) for Environmental Separation and Temperature Control and up to 10 feet (3048 mm) for Flying Insect Control.

      - Discharge Nozzle: Adjustable air foil vanes with a plus/minus 40-degree sweep front to back.

      - Air Velocity at Nozzle:

SPECIFIER NOTE – Select one of the following paragraphs for the model required and delete the ones not required. If more than one type is required show the location of each type on the Drawings or on the Schedule at the end of this Section.

        - PH10 36-1: 36 Inch (915 mm) Wide Units: 1947 feet/min (9.9 m/s) single 1/2HP motor/fan assembly.

        - PH10 42-1: 42 Inch (1065 mm) Wide Units: 1806 feet/min (9.2 m/s) single 1/2HP motor/fan assembly.

        - PH10 48-1: 48 Inch (1220 mm) Wide Units: 1632 feet/min (8.3 m/s) single 1/2HP motor/fan assembly.

        - PH10 60-2: 60 Inch (1524 mm) Wide Units: 2217 feet/min (11.3 m/s) single 1/2HP motor/fan assembly.

        - PH10 72-2: 72 Inch (1830 mm) Wide Units: 1947 feet/min (9.9 m/s) two 1/2HP motor/fan assemblies.

        - PH10 84-2: 84 Inch (2133 mm) Wide Units: 1806 feet/min (9.2 m/s) two 1/2HP motor/fan assemblies.

        - PH10 96-2: 96 Inch (2440 mm) Wide Units: 1632 feet/min (8.3 m/s) two 1/2HP motor/fan assemblies.

        - PH10 108-3: 108 Inch (2743 mm) Wide Units: 1947 feet/min 9.9 m/s) three 1/2HP motor/fan assemblies.

        - PH10 120-4: 120 Inch (3050 mm) Wide Units: 2217 feet/min (11.3 m/s) three 1/2HP motor/fan assemblies.

        - PH10 144-4: 144 Inch (3660 mm) Wide Units: 1947 feet/min (9.9 m/s) four 1/2HP motor/fan assemblies.

      - Air Speed at Floor: Minimum of 400 fpm (2 m/s) at 3 feet (914 mm) from the floor.

      - Air Inlet Grille and Filters:

SPECIFIER NOTE – Select one of the following air inlet type paragraphs and delete the ones not required.

        - Location: Bottom/

          - Filter: Cleanable polyester filter, 1 inch (25.4 mm).

        - Type: Fixed air intake grille

SPECIFIER NOTE – Include the following optional filter paragraph if required and delete if not required.

          - Filter: Aluminum mesh, 1/4 inch (6.4 mm), washable.

        - Type: Filter Only as follows:

SPECIFIER NOTE – Include one of the following optional filter paragraphs as required and delete those not required.

          - Filter: Flat bank 1 inch, disposable.

          - Filter: Aluminum mesh, 1/4 inch (6.4 mm), washable

        - Speed: 2550 cu ft/min (1200 L/s), minimum, per motor/fan assembly

      - Sound Pressure Level At 10 feet (3 m) From Nozzle:

SPECIFIER NOTE – Select one of the following paragraphs and delete the ones not required. Coordinate selection with the Model specified above.

        - Single Motor/Fan Units: 66 dBA.

        - Two Motor/Fan Units: 68 dBA.

        - Three Motor/Fan Units: 71 dBA.

        - Four Motor/Fan Units: 73 dBA

SPECIFIER NOTE – Select the optional components required from the following paragraphs for the air curtains specified. If more than one type of air curtain or component is required, indicate the location of each curtain and the components required for each location on the Drawings or on the Schedule at the end of this Section. Contact Mars Air Systems for specialty steam and hot water heaters other than those included in the specification.

  - COMPONENTS

    - Electric Heaters: Provide complete with motor control panel factory mounted to air curtain housing, and thermostat to be field installed.

      - Temperature limit controller.

      - Thermostat: Wall-mounted, 24-Volt operation, with heater on/off selection.

      - Heating Coils: ETL approved as part of unit. Meets NEC and CEC tested by ETL Certified to conform to UL2021(US) and CSA22.2 (Canada) Standards. Factory mounted on the discharge end of the motor fan assembly and located within the nozzle outlet.

    - Steam Heaters: Provide finned tube steam coils for field mounting on air intake side of the air curtain cabinet with opposite end connections.

      - Meets NEC and CEC tested by ETL Certified to conform to UL1995(US) and CSA22.2 (Canada) Standards.

SPECIFIER NOTE – Select one of the following two paragraphs.

      - Output: Air curtain manufacturer's standard, one-row coils.

      - Output: Air curtain manufacturer's standard, two-row coils.

      - Coils: Certified in accordance with AHRI 410.

SPECIFIER NOTE – Delete two of the following three connections paragraphs.

      - Connections: Opposite end.

      - Connections: Same end, right hand.

      - Connections: Same end, left hand.

      - Casing: One-piece unpainted galvanized steel, bolted to air curtain housing.

      - Supply and return fittings on ends of casing.

SPECIFIER NOTE – Thermostat is optional. Delete if not required.

      - Thermostat: Wall-mounted, 110-Volt operation, with heater on/off selection.

    - Hot Water Heaters: Provide finned tube water coils for field mounting on air intake side of the air curtain cabinet with opposite end connections.

      - Meets NEC and CEC tested by ETL Certified to conform to UL1995(US) and CSA22.2 (Canada) Standards.

SPECIFIER NOTE – Delete one of the following two output paragraphs.

      - Output: Air curtain manufacturer's standard, one-row coils.

      - Output: Air curtain manufacturer's standard, two-row coils.

      - Coils: Certified in accordance with AHRI 410.

SPECIFIER NOTE – Delete two of the following six connections paragraphs.

      - Connections: Opposite end.

      - Connections: Same end, right hand.

      - Connections: Same end, left hand.

      - Casing: One-piece unpainted galvanized steel, bolted to air curtain housing.

      - Supply and return fittings on ends of casing.

SPECIFIER NOTE – Thermostat is optional. Delete if not required.

      - Thermostat: Wall-mounted, 110-Volt operation, with heater on/off selection.

SPECIFIER NOTE – Select one of the following Motor Control Panel paragraphs as required and delete the ones not required. The first paragraph is for Unheated Units, the second is for Electric Heated Units and the third is for Steam and Hot Water Heated Units.

    - Motor Control Panels for Unheated Units: Recommended for all three-phase units and single-phase units with combined motor capacities of more than 1 HP whenever a door limit switch is used to automatically start and stop the air curtain. Provide motor control panels as follows:

SPECIFIER NOTE – Delete all but one of the following three mounting paragraphs. Standard mounting offering for motor control panel is shipped loose for field mounting.

      - Mounting: Shipped loose to be field mounted.

      - Mounting: Factory mounted on right hand side of air curtain housing.

      - Mounting: Factory mounted on left hand side of air curtain housing.

      - Electrical components UL/CUL listed.

      - Panels UL 508A listed.

      - Optional Digital Programmable Controller:

        - WiFi enabled controller for wireless interface with field supplied smartphone, tablet or computer

        - No download or app required for wireless interface

        - Wireless control range up to minimum of 50 feet from controller

        - Fully factory assembled and wired inside the air curtain for easy field installation

        - Optional remote mounted high resolution 7” Color LCD Display with resistive touchscreen technology

        - Fully programmable controller

        - Pre-set and fully customizable programs

        - Time delay (Passive & Adaptive)

        - 24/7/365 timer

        - Maintenance schedule alerts

        - Password protected

        - Low voltage control signal for door activation

        - Multispeed fan control

        - Optional VFD compatible with 0-10VDC output

        - Optional Integrated BMS controls

        - Optional BACnet MS/TP

        - Optional BACnet IP

        - Optional adaptive fan speed control based on existing field conditions. Field mounted outdoor temperature sensors required.

    - Motor Control Panels for Electric Heated Units: Motor Control Panel is included for all electric heated units. Thermostat is provided for field installation. Provide motor control panel as follows:

SPECIFIER NOTE – Delete all but one of the following three mounting paragraphs. Standard factory mounting for motor control panels on electric heated units is on the inside of air curtain.

      - Mounting: Factory mounted on the inside of air curtain housing.

      - Mounting: Factory mounted on right hand side of air curtain housing.

      - Mounting: Factory mounted on left hand side of air curtain housing.

      - Electrical components UL/CUL listed.

      - Optional Digital Programmable Controller:

        - WiFi enabled controller for wireless interface with field supplied smartphone, tablet or computer

        - No download or app required for wireless interface

        - Wireless control range up to minimum of 50 feet from controller

        - Fully factory assembled and wired inside the air curtain for easy field installation

        - Optional remote mounted high resolution 7” Color LCD Display with resistive touchscreen technology

        - Fully programmable controller

        - Pre-set and fully customizable programs

        - Time delay (Passive & Adaptive)

        - Factory Integrated temperature control sensors. No external thermostat required.

        - Heat on Demand Mode to regulate the space temperature

        - Summer-Winter modes

        - 24/7/365 timer

        - Maintenance schedule alerts

        - Password protected

        - High temperature lock from fan failure

        - Low voltage control signal for door activation

        - Multispeed fan control

        - Optional VFD compatible with 0-10VDC output

        - Optional Integrated BMS controls

        - Optional BACnet MS/TP

        - Optional BACnet IP

        - Optional adaptive fan speed control and heat control based on existing field conditions. Field mounted outdoor temperature sensors required.

    - Motor Control Panels For Hot Water and Steam Heated Units: Recommended for all three-phase units and single phase units with combined motor capacities of more than 1HP whenever a door limit switch is used to automatically start and stop the air curtain. Provide motor control panels as follows:

SPECIFIER NOTE – Delete all but one of the following three mounting paragraphs.

      - Mounting: Shipped loose to be field mounted.

      - Mounting: Factory mounted on right hand side of air curtain housing.

      - Mounting: Factory mounted on left hand side of air curtain housing.

      - Provide with remote mount thermostat for field installation.

      - Electrical components UL/CUL listed.

      - Panels UL 508A listed.

      - Optional Digital Programmable Controller:

        - WiFi enabled controller for wireless interface with field supplied smartphone, tablet or computer

        - No download or app required for wireless interface

        - Wireless control range up to minimum of 50 feet from controller

        - Fully factory assembled and wired inside the air curtain for easy field installation

        - Optional remote mounted high resolution 7” Color LCD Display with resistive touchscreen technology

        - Fully programmable controller

        - Connect and control via any web browser

        - Factory built wireless router with over 50 feet range

        - Pre-set and fully customizable programs

        - Time delay (Passive & Adaptive)

        - Factory Integrated temperature control sensors. No external thermostat required.

        - Heat on Demand Mode to regulate the space temperature

        - Summer-Winter modes

        - 24/7/365 timer

        - Maintenance schedule alerts

        - Password protected

        - High temperature lock from fan failure

        - Low voltage control signal for door activation

        - Multispeed fan control

        - Optional VFD compatible with 0-10VDC output

        - Optional Integrated BMS controls

        - Optional BACnet MS/TP

        - Optional BACnet IP

        - Optional adaptive fan speed control and heat control based on existing field conditions. Field mounted outdoor temperature sensors required.

    - Door-Activated Limit switch(s): Provide, field installed 250-Volts, 20 amps limit switch to control air curtain(s) as follows; Automatic on/off control, activates air curtain when door is opened and turns off when door is closed. Provide limit switch for direct control one 1 HP or up to two 1/2 HP single phase motors without a separate control panel. Provide a separate control panel for three-phase motors and/or units exceeding 1 HP, 250-Volts or 20 amps controlled by a limit switch.

      - Type: Combination plunger/roller switch for swing and sliding doors.

SPECIFIER NOTE – Delete three of the following four paragraphs to suit enclosures for incidental contact, protection against weather and corrosive exposure and explosion proof as required.

        - Provide limit switches with NEMA 1 (20 amps) ratings in locations indicated.

        - Provide limit switches with NEMA 4X (10 amps) ratings in locations indicated.

        - Provide limit switches with NEMA 4X (15 amps) ratings in locations indicated.

        - Provide limit switches with NEMA 7 (10 amps) ratings in locations indicated.

      - Type: Magnetic reed switch and actuator for swing and sliding doors. Industrial floor mounted or surface mounted switches for roll up doors.

      - Operation for Unheated Units: Automatic on/off control, on when door is opened, off when door is closed.

      - Operation for Heated Units: Automatic on when door is opened, off after time delay period after door is closed, maintaining heat in the event door is opened within time delay period. Field adjustable from 1 to 17 minutes.

    - Provide mounting hardware as required for the opening.

- EXECUTION

  - EXAMINATION

    - Verify that required utilities are in correct location and are of correct capacities for specified products.

    - Verify openings to receive air curtains are plumb, level, square, accurately aligned, correctly located, and in tolerance.

    - Examine surfaces to receive air curtains. If surface preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

  - INSTALLATION

SPECIFIER NOTE – Indicate the mounting location(s) on the Drawing or on the Schedule at the end of this Section. Units are typically wall mounted horizontally above the door opening. Units can also be suspension mounted from the ceiling or vertically mounted alongside the opening. Heated units must be mounted on the inside or protected side of the opening.

    - Install air curtains in accordance with approved shop drawings and manufacturer's printed installation instructions.

    - Install air curtains plumb, level, square, true to line, and weathertight, without warp or rack.

    - Anchor air curtains securely in place to supports.

    - Coordinate with sheet metal flashing as specified in Section 07 62 00.

    - Install joint sealants as specified in Section 07 92 00.

    - Coordinate with electrical power as specified in Section 26 05 00.

    - Install door limit switches and adjust for correct operation.

    - Provide connection to piped services and utilities as specified in Section 22 10 00 and 23 21 00.

  - FIELD QUALITY CONTROL

    - Adjust air curtains to function properly.

    - Adjust air foil vanes located within the discharge nozzle as required for prevailing conditions at each opening.

    - Check heated air curtain performance on a calm day by measuring air temperature 6 inches off the floor. Optimal reading is halfway between the temperature inside and outside the building.

  - CLEANING

    - Clean air curtains promptly after installation in accordance with manufacturer's instructions.

    - Repair minor damages to finish in accordance with manufacturer's instructions and as approved by Architect.

    - Remove and replace damaged components that cannot be successfully repaired as determined by Architect.

  - PROTECTION

    - Protect materials and finish from damage until substantial completion.

SPECIFIER NOTE – For facilities with multiple types and sizes of air curtains use an Air Curtain Schedule to list requirements for each size, type, HP, and power requirements of air curtain(s) required. Delete if not required.

  - SCHEDULES

    - Refer to Air Curtain Schedule appended to this section.

END OF SECTION